## IEC62559-2
1 Description of the use case | Instructions are provided as comments in the rows
1.1 Name of use case
Use case identification
| ID | UC5
| Area/ Domain(s)/ Zone(s) | Distribution DER / Field, Station, Operation
| Name of use case | Volt-VAr optimization with increasing RES generation
1.2 Version management
| Version No. | 0.9
| Date | 25.11.2020
| Name of author(s) | Nikolaos Livanos, Vaggelis Alifragkis, Georgios Stravopodis
Changes
Approval status
1.3 Scope and objectives of use case
| Scope | The scope of the proposed Use Case is to implement Volt-VAr optimization approaches in the context of the eBalance+ project, by means of intelligent management units and optimization algorithms in the application field (i.e. Distribution Substations, RES, etc.).
| Objective(s) | a. To demonstrate the impact of Volt/VAr optimization on voltage stability b. To demonstrate the impact of Volt/VAr optimization on technical power losses c. To demonstrate the impact of Volt/VAr optimization on RES curtailment d. To demonstrate the performance of Volt/VAr optimization both with a centralized and a distributed implementation with respect to possible failures in both approaches.
Related business case(s)
1.4 Narrative of use case
| Short description | The proposed Use Case refers to Volt-VAr optimization in a Power Distribution Grid incorporating DER (mainly RES), aiming to apply and demonstrate concepts and technologies of the eBalance+ project. The Use Case shall evaluate a specific distribution grid topology (TBD) in three different setups: 1. Laboratory Numerical Simulation, 2. Laboratory Simulation with Hardware-in-the-Loop (of eBalance+ management units), 3. Actual performance in project’s demo site(s). Regarding setup 3 (demo site) certain modifications in the distribution grid topology are anticipated, mainly due to the limitations of access to grid assets, as well as the limitations to intervene in the present control schemes. Two core scenarios will be presented: 1. Centralized, 2. Distributed. In the Centralized Scenario the Volt-VAr control is arbitrated and executed in the (A)DMS system (assumed to exist). The information is exchanged via the eBalance+ middleware and the MVGMU, LVGMU and DERMU devices (management units) are mainly used for communication interfacing and as remote terminal points (RTUs). In the Distributed scenario, the Volt-Var control is performed in the MVGMU device as an alternate scenario in case of central systems failures. As in the Centralized scenario, the LVGMU and DERMU are used for communication interfacing, again following eBalance+ middleware information routes.
| Complete description | The present Use Case aims on the following: • Increased RES penetration in power distribution grids causes congestion and effective Volt-VAr optimization can intelligently manage RES to alleviate the problem. • An information/communication middleware (ebalance+) adopted by intelligent management units installed in the Operation, Station, and Field domains (following SGAM notation) can increase overall system resilience by means of automatic re-configuration and continuity of Volt-VAr service. • Intelligent management units in the Station and Field domains (e.g. MVGMU) are able to provide optimized Volt-VAr service. • Distributed intelligence could support Volt-VAr optimization approaches • Simulate respective Volt-Var optimization approaches • Apply Hardware-in-the-loop of the eBalance+ intelligent devices in the above simulations • Apply selected Volt-VAr optimization scenarios in the eBalance+ pilot installations • Measure and analyze performance in the demo sites The Volt-VAr Use Case is based on the following methodology: 1. Define a configurable power distribution grid topology a. Based on detailed analysis the topology may incorporate assets, such as: HV/MV Substation, Substation Capacitor Bank, Substation Transformer with On-Load TAP changer, MV RES, MV/LV Transformer with Voltage Regulator, MV Line Capacitors, LV RES, MV Loads, LV Loads, etc. b. The topology shall define the connections between the assets and perhaps possible reconfigurations (e.g. power switches, etc.) c. The RES generation shall be configurable (e.g. define three RES penetration scenarios: 50%, 100%, 200%). d. Part of the overall topology will be similar to the demo installation topologies 2. Define various congestion situations 3. Define specific optimization objective functions: Voltage Range, Power Loss Reduction, Minimum RES Curtailment 4. Define specific KPIs to support evaluation, comparisons and reporting: Voltage Violations (Frequency, Duration, Number, Excess), Power Losses, RES Energy, (optional KPIs depending on available control of assets: number of capacitor transitions, number of OLTC transitions, etc.) 5. Implement two scenarios: a. Centralized Volt-VAr: the solver is executed in the (A)DMS at the DSO’s Operation Center b. Distributed Volt-VAr: the solver is executed in the intelligent device in the Primary Distribution Substation (e.g. MVGMU) 6. Evaluate and compare the two scenarios 7. Evaluate and compare the grid’s performance before and after the application of optimization 8. The Use Case shall be implemented according to the following phases: a. Phase 1: Analysis, definitions and laboratory numerical simulations b. Phase 2: Laboratory simulations with Hardware-in-the-loop (e.g. MVGMU, LVGMU, DERMU in the simulation loop) c. Phase 3: Demo sites operations
1.5 Key performance indicators (KPI)
| ID | KPI.01 | KPI.02 | KPI.03
| Name | Reduction of voltage violations | Technical losses reduction | RES energy injection maximization
| Description | Based on the application of the Voltage Range objective function, this KPI measures the Frequency, Count and Duration of Voltage Violations per bus | Based on the application of the Power Loss Reduction objective function, this KPI measures the reduction of power losses on the overall grid | Based on the application of Minimum RES curtailment, measure the total energy supplied by RES to the grid
| Reference to mentioned use case objectives | Voltage Range | Power Loss Reduction | Minimum RES Curtailment
1.6 Use case conditions
| Assumptions | The number of capacitor and OLTC switches are not taken into account | Failures or communication loss on Capacitor Bank Controller, On-Load Tap Changer Controller, Line Voltage Regulator, Line Capacitor, are not taken into account | DSO and DER operators always accept the Volt/Var optimization solution. | When communication loss occurs, all the controllable elements (Capacitor Bank Controller, On-Load Tap Changer Controller, Line Voltage Regulator, Line Capacitor) remain operational | All pre-assumptions plus: All communication connections on the grid are operating within their parameters in order to send/receive data and control signals | All pre-assumptions | All pre-assumptions plus: All communication connections on the grid are operating within their parameters in order to send/receive data and control signals | All pre-assumptions
| Prerequisites |  |  |  |  | The Volt/Var Control Algorithm (VVC)is configured correctly according to VVC.CONF | The Algorithm is configured correctly according to VVC.CONF | The Algorithm is configured correctly according to VVC.CONF | The Algorithm is configured correctly according to VVC.CONF
1.7 Further information to the use case for classification/mapping
Relation to other use cases
| Level of depth | Detailed Use Case
| Prioritisation | Mandatory
| Generic, regional or national relation | Generic
| Nature of the use case | Technical
| Further keywords for classification | Advanced Distribution Management System, optimisation, simulation, RES, substation
1.8 General remarks
General remarks
2 Diagrams of use case
| Diagram name | Sequence Diagram - Scenario 1 part 1/2 | Sequence Diagram - Scenario 1 part 2/2 | Sequence Diagram - Scenario 2 | SGAM - Component Layer - Scenario 1 | SGAM - Component Layer - Scenario 2 | SGAM - Function Layer - Scenario 1 | SGAM - Function Layer - Scenario 2 | SGAM - Communication Layer - Scenario 1 | SGAM - Communication Layer - Scenario 2 | SGAM - Information Layer - Scenario 1 | SGAM - Information Layer - Scenario 2 | SGAM - Buisness Layer
| Diagram type | scenarios_flowchart | scenarios_flowchart | scenarios_flowchart | other | other | other | other | other | other | other | other | other
| Diagram URI type | image | image | image | image | image | image | image | image | image | image | image | image
| Diagram URI value | Sequence_Diagram-Sc1-part1.png | Sequence_Diagram-Sc1-part2.png | Sequence_Diagram-Sc2.png | Component_layer_scenario1.png | Component_layer_scenario2.png | Function_layer_scenario1.png | Function_layer_scenario2.png | Communication_layer_scenario1.png | Communication_layer_scenario2.png | Information_layer_scenario1.png | Information_layer_scenario2.png | Buisness_layer.png
3 Technical details
3.1 Actors
| Grouping | DSO | Industrial partner | Legal Client | DER installation | Network device(s) | IT/OT | IT/OT | IT/OT
Group description
| Actor name | DSO / Utility | Service Provider | DER Owner | DER installation(s) | MVGMU, LVGMU, DERMU | SCADA, (A)DMS | DMS.VVC | MVGMU.VVC
| Actor type | Role | Role | Role | System(s) | System(s) | Systems | System | System
| Actor description | Responsible for operating, ensuring the maintenance of and, if necessary, developing the distribution system in a given area | Industrial partner involved in the ebalance+ project providing providing management units and algorithms | The owner of DER installation (see below) or the appointed representative that allows flexibility management | Small generation plant(s) (mainly of renewable energy) owned by a legal person | All devices placed on MV/LV network for monitoring or gathering information on grid's situation or electrical parameters values. It also includes the IS associated | All the hardware and software associated, used at power command to control and monitor the network | The software that performs the algorithms and produces the desired results. Operates at the DMS level | The software that performs the algorithms and produces the desired results. Operates at the MVGMU level
| Further information specific to this use case | Responsible for accepting the results of the DMS.VVC or MVGMU.VVC in order for them to be applied to the grid. |  | Responsible for accepting the results of the DMS.VVC or MVGMU.VVC in order for them to be applied to the grid.
3.2 References
Name
No.
References type
Reference
Status
Impact on use case
Originator/organisation
Link
4 Step by step analysis of use case | 4.1 Overview of scenarios
Scenario conditions
| No. | PS1 | AS1
| Scenario name | Centralized Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability
| Scenario description | The optimization logic is performed on the Distribution Management System level by collecting readings from the complete underlying grid. In turn control actions computed by the algorithm are distributed to the complete grid. The Primary scenario is separated in the following cases: 1. Nominal scenario, where the grid experiences no failures 2. DMS failure 3. MVGMU failure 4. LVGMU failure 5. DERMU failure | The optimization logic is performed on the Medium Voltage Grid level by collecting readings from the complete underlying grid. In turn control actions computed by the algorithm are distributed to the complete grid
| Primary actor | DMS/SCADA | MVGMU
| Triggering event | Automated/Periodic execution | Automated/Periodic execution
| Pre-condition | The algorithm is configured according to the VVC.CONF Information point. | The algorithm is configured according to the VVC.CONF Information point.
| Postcondition | The corresponding KPIs of the selected objective are within acceptable limits. | The corresponding KPIs of the selected objective are within acceptable limits.
4.2 Steps – Scenarios
| Scenario name: | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Centralized Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability | Distributed Volt/Var Optimization with RES Variability
| Step No. | 1.1 | 1.2 | 1.3 | 1.4 | 2.1 | 3.1 | 3.2 | 3.3 | 3.4 | 4.1 | 4.2 | 4.3 | 4.4 | 5.1 | 5.2 | 5.3 | 5.4 | 0 | 1.1 | 1.2 | 1.3 | 1.4 | 2.1 | 2.2 | 2.3 | 2.4 | 3.1 | 4.1 | 4.2 | 4.3 | 4.4 | 5.1 | 5.2 | 5.3 | 5.4
| Event | Periodic Execution /No Failures – Set Inputs | Periodic Execution – Optimization | Periodic Execution – Get Outputs | Reporting | DMS Failure Set Inputs | MVGMU Failure Set Input | Periodic Execution – Optimization | Periodic Execution – Get Outputs | Reporting | LVGMU Failure Set Input | Periodic Execution – Optimization | Periodic Execution – Get Outputs | Reporting | DERMU Failure Set Input | Periodic Execution – Optimization | Periodic Execution – Get Outputs | Reporting | Configuration | Periodic Execution /No Failures – Set Inputs | Periodic Execution – Optimization | Periodic Execution – Get Outputs | Reporting | DMS Failure Set Inputs | Periodic Execution – Optimization | Periodic Execution – Get Outputs | Reporting | MVGMU Failure Set Input | LVGMU Failure Set Input | Periodic Execution – Optimization | Periodic Execution – Get Outputs | Reporting | DERMU Failure Set Input | Periodic Execution – Optimization | Periodic Execution – Get Outputs | Reporting
Name of process/activity
| Description of process/activity | DMS sets all the required input to VVC | VVC performs optimization algorithm on given inputs (Optimum Power flow) | VVC sends control signals based on results | VVC computes and reports KPI compliance (continued process across multiple runs) | DMS.VVC tries to collect inputs but communication has failed. (Please see AS1) | DMS.VVC tries to collect all inputs but MVGMU fails to provide | VVC performs optimization algorithm on given inputs (Optimum Power flow) without input from MVGMU | VVC sends control signals based on results | VVC computes and reports KPI compliance (continued process across multiple runs) | DMS.VVC tries to collect all inputs but LVGMU fails to provide | VVC performs optimization algorithm on given inputs (Optimum Power flow) without input from LVGMU | VVC sends control signals based on results | VVC computes and reports KPI compliance (continued process across multiple runs) | DMS.VVC tries to collect all inputs but DERMU fails to provide | VVC performs optimization algorithm on given inputs (Optimum Power flow) without input from DERMU | VVC sends control signals based on results | VVC computes and reports KPI compliance (continued process across multiple runs) | MVGMU Configures VVC according to VVC.CONF | MVGMU sets all the required input to VVC | VVC performs optimization algorithm on given inputs (Optimum Power flow) | VVC sends control signals based on results | VVC computes and reports KPI compliance (continued process across multiple runs) | MVGMU.VVC tries to collect inputs but DMS has failed | VVC performs optimization algorithm on given inputs (Optimum Power flow) without input from MVGMU | VVC sends control signals based on results | VVC computes and reports KPI compliance (continued process across multiple runs) | MVGMU.VVC tries to collect all inputs but MVGMU fails to provide | MVGMU.VVC tries to collect all inputs but LVGMU fails to provide | VVC performs optimization algorithm on given inputs (Optimum Power flow) without input from LVGMU | VVC sends control signals based on results | VVC computes and reports KPI compliance (continued process across multiple runs) | MVGMU.VVC tries to collect all inputs but DERMU fails to provide | VVC performs optimization algorithm on given inputs (Optimum Power flow) without input from DERMU | VVC sends control signals based on results | VVC computes and reports KPI compliance (continued process across multiple runs)
| Service | GET | EXECUTE | CHANGE | REPORT | GET | GET | EXECUTE | CHANGE | REPORT | GET | EXECUTE | CHANGE | REPORT | GET | CHANGE | CHANGE | REPORT | CREATE | GET | EXECUTE | CHANGE | REPORT | GET | EXECUTE | CHANGE | REPORT | GET | GET | EXECUTE | CHANGE | REPORT | GET | CHANGE | CHANGE | REPORT
| Information producer (actor) | MVGMU, LVGMU, DERMU | N/A | VVC | VVC | N/A | LVGMU, DERMU | N/A | VVC | VVC | MVGMU, LVGMU | N/A | VVC | VVC | MVGMU, LVGMU | N/A | VVC | VVC | MVGMU | MVGMU, LVGMU, DERMU | N/A | VVC | VVC | MVGMU, LVGMU, DERMU | N/A | VVC | VVC | N/A | MVGMU, DERMU | N/A | VVC | VVC | MVGMU, LVGMU | N/A | VVC | VVC
| Information receiver (actor) | VVC | VVC | MVGMU, LVGMU, DERMU | DMS | VVC | VVC | VVC | LVGMU, DERMU | DMS | VVC | VVC | MVGMU, DERMU | DMS | VVC | VVC | MVGMU, LVGMU | DMS | MVGMU.VV | VVC | VVC | MVGMU, LVGMU, DERMU | MVGMU | VVC | VVC | MVGMU, LVGMU, DERMU | MVGMU | VVC | VVC | VVC | MVGMU, DERMU | MVGMU | VVC | VVC | MVGMU, LVGMU | MVGMU
| Information exchanged (IDs) | VVC.IN | N/A | VVC.OUT | VVC.RPT | VVC.IN | VVC.IN | N/A | VVC.OUT | VVC.RPT | VVC.IN | N/A | VVC.OUT | VVC.RPT | VVC.IN | N/A | VVC.OUT | VVC.RPT | VVC.CONF | VVC.IN | N/A | VVC.OUT | VVC.RPT | VVC.IN | N/A | VVC.OUT | VVC.RPT | VVC.IN | VVC.IN | N/A | VVC.OUT | VVC.RPT | VVC.IN | N/A | VVC.OUT | VVC.RPT
| Reference to Scenario number | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | PS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1 | AS1
5 Information exchanged
| Requirement, R-Ids | [VVC.001] The execution period shall be expressed in seconds [VVC.002] The topology provided to the VVC function shall include the following: 1. Line Specification (length, conductance) 2. Load Specification 3. Generator Specification (rated power) 4. RES Generator Specification (rater power, inverter specification) 5. Transformer Specification (voltage step, losses) 6. Capacitor specification (capacitance) 7. TAP Specification (voltage Step) | [VVC.003] The VVC function shall get as input the Distribution Grid state, which is: 1. Voltage (V) 2. Active Power (MW) 3. Reactive Power (MW) 4. TAP Position (number) 5. Capacitor Bank Status (on/off per capacitor) [VVC.004] The VVC function shall get as input the RES state, which is: 1. Voltage (V) 2. Active Power (MW) 3. Reactive Power (MVar) [VVC.005] All the inputs shall be provided by the SCADA in the case of DMS deployment (scenario 1) [VVC.006] All the inputs shall be provided by the MVGMU RTU in the case of MVGMU deployment (scenario 2) [VVC.007] All the inputs shall be provided Inputs that have no value for any reason shall be denoted as “null” | [VVC.008] The VVC function shall calculate the following: 1. Capacitor Bank New Status (on/off per capacitor) 2. TAP Position (number) 3. Line Capacitor Status (on/off flag) 4. RES Set-Point (desired power factor per RES source) [VVC.009] All outputs shall be provided to the SCADA in the case of DMS deployment [VVC.010] All outputs shall be provided to the MVGMU.RTU in the case of MVGMU deployment [VVC.011] Any not-set values shall be denoted by “null” | [VVC.012] The VVC shall be able to report the value of its KPIs [VVC.013] The KPIs shall be measured by the VVC function after it provides outputs. | [VVC.014] The MVGMU.RTU shall provide its measurements to the SCADA (scenario 1) [VVC.015] The MVGMU shall provide its measurements to the VVC function directly (scenario 2) [VVC.016] The measurements of the MVGMU.RTU shall be: 1. Capacitor Bank Status (on/off per capacitor) 2. Tap Measurement (number) 3. Voltage (V) 4. Reactive Power (MVAr) 5. Active Power (MW) | [VVC.017] The MVGMU shall receive control signals from the SCADA as calculated by the VVC function (scenario 1) [VVC.018] The MVGMU shall receive control signals from the VVC function directly (scenario 2) [VVC.019] The MVGMU.RTU shall support the following control signals: 1. TAP Position (number) 2. Capacitor State (on/off per capacitor) | [VVC.020] The LVGMU.RTU shall provide its measurements to the SCADA (scenario 1) [VVC.021] The LVGMU shall provide its measurements to the MVGMU (scenario 2) [VVC.022] The measurements of the LVGMU.RTU shall be: 1. Line Capacitor Status (on/off flag) 2. Line Voltage (V) 3. Reactive Power (MVAr) 4. Active Power (MW) | [VVC.023] The LVGMU shall receive control signals from the SCADA as calculated by the VVC function (scenario 1) [VVC.024] The LVGMU shall receive control signals from the MVGMU (scenario 2) [VVC.025] The LGMU.RTU shall support the following control signals: 1. Capacitor State (on/off flag) 2. Live Voltage Regulator Set-Point (Power Factor) | [VVC.026] The DERMU.RTU shall provide its measurements to the SCADA (scenario 1) [VVC.027] The DERMU shall provide its measurements to the MVGMU (scenario 2) [VVC.028] The measurements of the DERMU.RTU shall be: 1. Line Voltage (V) 2. Reactive Power (MVAr) 3. Active Power (MW) | [VVC.029] The DERMU shall receive control signals from the SCADA as calculated by the VVC function (scenario 1) [VVC.030] The DERMU shall receive control signals from the MVGMU (scenario 2) [VVC.031] The DERMU.RTU shall support the following control signals: 1. RES Set-Point (Power Factor per RES)
| Information exchanged, ID | VVC.CONF | VVC.IN | VVC.OUT | VVC.RPT | MGVMU.OUT | MGVMU.CTRL | LVGMU.OUT | LVGMU.CTRL | DERMU.OUT | DERMU.CTRL
| Name of information | VVC Configuration | VVC Input Execution Parameters | VVC Output Results | VVC Reporting | MGVMU RTU Outputs/Measurements | MGVMU RTU Control Input | LVGMU Output measurements | LVGMU RTU Control Input | DERMU Output measurements | DERMU Control Input
| Description of information exchanged | Describes all the configuration options needed to be set to the VVC from the SCADA or RTU system that contains the VVC. These options only need to be set once and are: 1. Grid Topology 2. Execution Period | Describes the Information needed for a Volt/Var execution loop to compute. These are provided by the SCADA or RTU system that contains the VVC and are the following: 1. Voltage (Distribution Grid) 2. Active Power (Distribution Grid) 3. Reactive Power (Distribution Grid) 4. TAP Position 5. Capacitor Bank Status 6. Voltage (RES) 7. Active Power (RES) 8. Reactive Power (RES) | Describes the results returned from the VVC after an execution loop. All results are returned to the SCADA or RTU system that contains the VVC which is then responsible to route them to the correct components. The output variables are: 1. Capacitor Bank New Status 2. TAP Position 3. Line Capacitor Status 4. RES set-points | Describes the metrics computed after operation for the evaluation target KPIs. These metrics are aggregated in a temporal and a statistical manner and are persistent across runs. The Metrics are: 1. Voltage Violations Frequency 2. Voltage Violations Count 3. Voltage Violation Duration 4. Voltage Violation Excess 5. Power Losses 6. RES Energy 7. RES Curtailment percentage 8. Number of Capacitor Switches 9. Number of OLTC Switches | Describes all the values measured and retrieved from the specific RTU. These are: 1. Capacitor Bank Measurement 2. Tap Measurement 3. Voltage 4. Reactive Power 5. Active Power | Describes all the elements that the specific RTU can control. These are: 1. TAP Position 2. Capacitor State | Describes all the values measured and retrieved from the specific RTU. These are: 1. Line Capacitor Status 2. Line Voltage Measurement 3. Reactive Power 4. Active Power | Describes all the elements that the specific RTU can control. These are: 1. Line Capacitor State 2. Voltage Regulator set-point | Describes all the values measured and retrieved from this unit. These are: 1. Voltage (RES) 2. Active Power (RES) 3. Reactive Power (RES) | Describes the controllable element of this unit which is: RES Set-Points.
Note on B5: Lucas Pons Bayarri: Use cases can be used in various areas (e.g. energy system). Within these areas, different domains are used to define/determine a more specific subgrouping. Zones might describe additional zones with an automation system or a reference architecture (SGAM). Experts in a particular field could suggest their set of domain (and zones) in order to provide a common understanding how to group use cases within a complex area. These predefined domains (and zones) can be chosen by the author of the use case (preselection). The author can select one or more domains and zone, comma separated, as it is usual that use cases are crossing different domains and zones. Example domains: Generation, transmission, DER, distribution, customer premises. Example zones: Process, field, station, operation, enterprise, market
Note on B7: Lucas Pons Bayarri: Insert one column per version. Do not remove previous columns in order to keep track of past versions. These set of field will be expanded in columns on any new version
Note on B10: Lucas Pons Bayarri: Comma-separated list
Note on B12: Lucas Pons Bayarri: will be used within the standardization organizations. The procedures for validation of use cases or actors will be defined in part 1 of this standard. EXAMPLE Similar to working draft, committee draft (CD) for comments, committee draft for vote (CDV), for voting (similar FDIS), final
Note on B16: Lucas Pons Bayarri: Comma separated list of related use cases
Note on B20: Lucas Pons Bayarri: Insert one column per KPI. This set of columns will expand in columns on any addtional KPI
Note on B25: Lucas Pons Bayarri: Insert as much assumptions and prerequisites as needed in columns. This set of rows will be expanded in columns
Note on B29: Lucas Pons Bayarri: Known relations to other use cases can be provided here if e.g. the use case is a more detailed one related to a high level use case, or it is an alternative to an existing use case. The type of relation like “include”, “extends”, “invokes” might be used in order to specify this relation in more detail.
Note on B30: Lucas Pons Bayarri: Use cases can be described on different levels (refer to IEC62559-1 for examples). Currently there is no fixed hierarchy for use cases defined, but some most common examples are provided. EXAMPLE High level use case, generic use case, specialised use cases.
Note on B31: Lucas Pons Bayarri: EXAMPLE: Obligatory/mandatory, optional, nice to have.
Note on B32: Lucas Pons Bayarri: On international level, the use case description might be generic enough to describe a use case in a more general way independently from the national or regional market design. But use cases might be used to describe regional or national specific circumstances like laws or even project-specific details. If the use case reflects those circumstances, it should be characterized accordingly. EXAMPLE National, "Country".
Note on B33: Lucas Pons Bayarri: This field can help to classify the main focus of the use case. EXAMPLE Technical/system use case, business use cases (e.g. market processes), political, test use cases.
Note on B35: Lucas Pons Bayarri: Insert one row per general remark of the use case. This row will be expanded by columns
Note on B36: Lucas Pons Bayarri: for further comments which are not considered elsewhere.
Note on B37: Lucas Pons Bayarri: Insert one column per diagram associated to this use case. This set of rows will be expanded by columns. Each diagram should be later uploaded to the github along with this template filled up. The name of the diagram files uploaded must match thr name specified in this section
Note on B39: Lucas Pons Bayarri: "domain_overview", "use_case_overview", "documentation", "scenarios_flowchart", "scenario_overview", "activities_flowchart", "activity_overview", "business_objects_overview", "role_model", "other" or nothing (default="other")
Note on B40: Lucas Pons Bayarri: "UMLDiagram", "image" or nothing
Note on B41: Lucas Pons Bayarri: Insert the name of the diagram exactly like the one that will be uploaded
Note on B43: Lucas Pons Bayarri: Insert one column per actor. These set of rows will be expanded by columns. The concept of an “actor” is very general and can cover: People (their roles or jobs), systems, databases, organizations, and devices involved in or affected by the use case: e.g. operators, system administrators, technicians, end users, service personnel, executives, SCADA system, real-time database, regional transmission operator (RTO), remote terminal units (RTU), intelligent electronic devices (IED) and even the power system. It is recommended to use actors as described in the ENTSO-E role model: https://eepublicdownloads.entsoe.eu/clean-documents/EDI/Library/HRM/Harmonised_Role_Model_2020-01.pdf
Note on B44: Lucas Pons Bayarri: The actor list can be grouped in order to provide a better overview. Naming convention: For complex groupings, the group name can be “dot-delimited”. EXAMPLE (area.domain.) main.sub.subsub. The grouping may follow the suggested domains/zones previous section
Note on B45: Lucas Pons Bayarri: Brief description of the group
Note on B46: Lucas Pons Bayarri: Actor name according to an existing taxonomy OR actor name especifically defined for this project
Note on B47: Lucas Pons Bayarri: If the actor is already defined in an existing and well-know actors taxonomy, just add here the name of the taxonomy (EXAMPLE: ENTSO-E role model). If not, here the type of actor should be provided
Note on B48: Lucas Pons Bayarri: In case the actor is not described in any existing taxonomy, the description mandatory. If the actor is already described ina taxonomy and the taxonomy is specified in the previos field, this field is not required
Note on B50: Lucas Pons Bayarri: Insert one column per reference. These set of rows will be expanded by columns.
Note on B53: Lucas Pons Bayarri: There are different reference types as shown in the examples above (e.g. standards, regulation, contract, others like publications)
Note on B54: Lucas Pons Bayarri: Any references shall be identified that might restrict or affect the design, understanding, and requirements of the use case, including contracts, regulations, policies, financial considerations, engineering constraints, pollution constraints, and other environmental quality issues
Note on B55: Lucas Pons Bayarri: e.g. NP, CD, CDV, FDIS, IS
Note on B56: Lucas Pons Bayarri: Where does the document influence the use case? e.g. copy right, IPR
Note on B57: Lucas Pons Bayarri: Who published the document?
Note on B58: Lucas Pons Bayarri: If available, a public link can be provided (e.g. to the IEC webstore for standards).
Note on B60: Lucas Pons Bayarri: Focuses on describing scenarios of the use case with a step-step analysis (sequence description).
Note on B61: Lucas Pons Bayarri: Insert one column per condition. These set of rows will be expanded by columns
Note on B65: Lucas Pons Bayarri: describes which actor(s) trigger(s) this scenario.
Note on B66: Lucas Pons Bayarri: describes which event(s) trigger(s) this scenario.
Note on B67: Lucas Pons Bayarri: Describes which condition(s) should have been met before this scenario happens.
Note on B68: Lucas Pons Bayarri: describes which condition(s) should prevail after this scenario happens The post conditions may also define “success” or “failure” conditions for each use case.
Note on B69: Lucas Pons Bayarri: Insert one column per step. These set of rows will be expanded by columns. For the scenario, all the steps performed shall be described going from start to end using simple verbs like – get, put, cancel, subscribe etc. Steps shall be numbered sequentially – 1, 2, 3 and so on. Should the scenario require detailed descriptions of steps that are also used by other use cases, it should be considered creating a new “sub” use case, then referring to that “subroutine” in this scenario.
Note on B70: Lucas Pons Bayarri: Refers to the name of one of the scenarios defined in the previous section
Note on B72: Lucas Pons Bayarri: The event that triggers the step. This might be completion of the previous step. EXAMPLE A human requesting the function, data being reported periodically, or a power system event
Note on B73: Lucas Pons Bayarri: Label that would appear in a process diagram. Action verbs should be used when naming activity.
Note on B74: Lucas Pons Bayarri: This describes what action takes place in this step. The focus should be less on the algorithms of the applications and more on the interactions and information flows between actors.
Note on B75: Lucas Pons Bayarri: This column identifies the nature of the information flow and the originator of the information. Available options are CREATE, GET, CHANGE, DELETE, CANCEL, EXECUTE derived from IEC 61968-100:2013, 6.2.2. Additionally, REPORT, TIMER and REPEAT are suggested. CREATE means that an information object is to be created at the Producer. GET (this is the default value if none is populated) means that the Receiver requests information from the Producer (default). CHANGE means that information is to be updated. Producer updates the Receiver’s information. DELETE means that information is to be deleted. Producer deletes information from the Receiver. CANCEL, CLOSE imply actions related to processes, such as the closure of a work order or the cancellation of a control request. EXECUTE is used when a complex transaction is being conveyed using a service, which potentially contains more than one verb. REPORT is used to represent transferral of unsolicited information or asynchronous information flows. Producer provides information to the Receiver. TIMER is used to represent a waiting period. When using the TIMER service, the Information Producer and Information Receiver fields shall refer to the same actor. REPEAT is used to indicate that a series of steps is repeated until a condition or trigger event. The condition is specified as the text in the “Event” column for this row or step. Following the word REPEAT, shall appear, in parenthesis, the first and last step numbers of the series to be repeated in the following form REPEAT(X-Y) where X is the first step and Y is the last step. These common service definitions are related to automation/information or communication systems. In case the use case template is applied in other domains, further services might be used and described.
Note on B76: Lucas Pons Bayarri: This identifies the producer or source of the information. This should be one of the actors in the reference template section.
Note on B77: Lucas Pons Bayarri: This identifies the receiver of the information. This should also be one of the actors identified above
Note on B78: Lucas Pons Bayarri: This describes briefly the information to be exchanged between the two actors – information producer and information receiver: – Input to the use case from some external sources that is not described in this use case. – Internal to the use case (e.g. between different applications and systems within the use case). – Output from the use case that will be used by other actors/entities not included in this use case. – This column should not contain technology issues/requirements. – It is allowed to list several information in one step, comma separated. – Summarizing the information exchanged between two actors based on the relevant set of use cases can characterize the needed communication/message payload. – Detailed information exchange should be identified using an ID (“Name of Information”). Such name should include the source namespace, if not referring to the by-default one. In this case, the column only contains the ID of the exchanged information which link to more details about the information in a separate table in the following template section 5 which is used for all steps of the use case. Here the information can use a short ID referring to template section 5 for further details. Several information exchanged IDs can be listed, comma separated.
Note on B79: Lucas Pons Bayarri: Refers to the Number of one of the scenarios defined in the previous section
Note on B80: Lucas Pons Bayarri: Insert one column per information item. These set of rows will be expanded by columns.
Note on B81: Lucas Pons Bayarri: the requirement id Can be used to define requirements referring to the information and not to the step as in the step by step analysis (see template section 6 below): EXAMPLE Data protection class corresponding to this information object.
Note on B82: Lucas Pons Bayarri: Unique ID which identifies the selected information in the context of the use case.
Note on B83: Lucas Pons Bayarri: Unique ID which identifies the selected information in the context of the use case.
Note on B84: Lucas Pons Bayarri: Brief description, in case a reference to existing data models/information classes should be added. Using existing canonical data models is recommended.

## Instructions
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.